# SOP-114: Centrifugal Pump Maintenance

Section 1. Purpose. This procedure defines inspection limits and required maintenance actions for centrifugal pumps in the cooling water system.

# Section 2. Wear tolerance limits

The maximum permitted impeller wear is 3.5 mm. Impeller wear above 3.5 mm means the impeller must be replaced before the pump returns to service.

Shaft vibration must not exceed 7.1 mm/s RMS. Readings between 4.5 and 7.1 mm/s require re-inspection within 30 days.

# Section 3. Required actions

If wear exceeds the limit: isolate the pump, tag out the motor, replace the impeller and wear rings, then run a 2 hour test before release.

If bearing temperature exceeds 85 degrees C the bearings must be replaced.

| Parameter | Limit | Action |
| --- | --- | --- |
| Impeller wear | 3.5 mm | Replace impeller |
| Bearing temp | 85 C | Replace bearings |